## Slide 1: Basic Electrical Engineering BEEE101L

## Slide 2: Module 6 Electrical Supply Systems & Safety
Concepts of electrical power generation, transmission and distribution systems;
Wiring;
Electrical safety;
Earthing;
Protective devices

## Slide 3: Electrical safety – insulation and fuses
Insulation is used to prevent ‘leakage’, and when determining what type of insulation should be used, the maximum voltage present must be taken into account.
For this reason, peak values are always considered when choosing insulation materials.
Fuses are the weak link in a circuit and are used to break the circuit if excessive current is drawn. Excessive current could lead to a fire.
Fuses rely on the heating effect of the current, and for this reason, r.m.s values must always be used when calculating the appropriate fuse size.

## Slide 4
Protective
Device
Help to ensure safe and healthy working conditions
Prevents damage to an electrical system.
Protect from the risk of injury.
It include circuit breaker and fuse.

## Slide 5: Protective Devices
Fuses
Circuit Breakers
FUSE
LOW VOLTAGE FUSE
REWIREABLE
CARTRIDGE
HIGH VOLTAGE FUSE
Miniature Circuit Breaker

## Slide 6: Fuses
It is a current interrupting device which breaks the circuit by fusing the element when current in the circuit exceeds certain value.
Fuse consist of two main parts:
  Fuse casing
  Fuse elements
Fuse casing may be made up of:
    Ceramics
    Glass
    Plastic
    Molded mica laminates

## Slide 7: Fuse Element Material
The materials used for fuse elements must be of low melting point , low ohmic loss ,high conductivity , low cost & free from deterioration.

## Slide 8
Rewireable Type
(Semi Enclosed Type or Kit-Kat Type)
This kind of fuse is most commonly used in the case of domestic wiring and small scale usage.
The main advantage of this type of fuse is that it is easy to install and also replace without risking any electrical injury. But there are certain shortcomings associated with it too.
Disadvantages:
Unreliable Operation
Lack Of Discrimination
Low Rupturing Capacity
No-Current-Limiting Features
Slow Speed Of Operation
Risk Of Flame & Fire

## Slide 9
Cartridge Type
(Totally Enclosed Type)
The level of sub division in this case includes:
  1.D type
  2.Link Type or High Rupturing Capacity
The fuse element is totally enclosed in an enclosed container, and it has metal contacts on both sides

## Slide 10: Link Type or High Rupturing Capacity
In such type of fuses, the fuse element carries the fault current for a long duration. If the fault is not clear, then the fuse element will melt and open the circuit. The major advantage of HRC fuse is that it clears the low as well as a high fault current.
HRC fuse has the high-speed operation and also does not require maintenance.
But the fuse element of the HRC fuses needs to be replaced after each operation, and it also produced the heat during the faults which will affect the operations of the nearby switches.

## Slide 11
High Voltage Fuse
High Voltage (HV) fuses are used in power system to protect the power transformer, distribution transformers and instrument transformer etc where circuit breakers may not be able to protect the system. High Voltage fuses are rated for more than 1500V and up to 13kV.

## Slide 12
Miniature circuit breaker (MCB)
MCB automatically switches off the electrical circuit during abnormal condition of the network means in over load condition as well as faulty condition.
MCB is much more sensitive to over current than fuse.
A circuit breaker is a manually or automatically operated electric switch designed to protect an electrical circuit from damage caused by overload or short circuit.

## Slide 13
Advantages
1. It automatically switches off the electrical circuit during abnormal condition of the network means in over load condition as well as faulty condition.
2. Handling MCB is more electrically safe than fuse.
3. Another advantage is, as the switch operating knob comes at its off position during tripping, the faulty zone of the electrical circuit can easily be identified.

## Slide 14
Grounding/Earthing

## Slide 15: Earthing and Grounding
The ‘earthing’ means the connection of non-current carrying part of the equipment to the earth. When the fault occurs in the system, then the potential of the non-current part of the equipment raises, and when any human or stray animal touch the body of the equipment, then they may get shocked.
In grounding, the current carrying parts are directly connected to the ground. The grounding provides the return path for the leakage current and hence protect the power system equipment from damage.
Earthing and grounding are similar terms. Still, these are having some differences.

## Slide 16
Improperly Grounded Appliance with Short
One milliampere: tingling sensation Ten milliamperes: nerves and muscles overloaded 200 milliamperes: potentially fatal; heart fibrillation 500 -1000 milliamperes: not necessarily fatal; heart will restart
One ampere or more: burn alive

## Slide 17
Grounded Appliance

## Slide 18: Grounding
The PRIMARY goal of the grounding – SAFETY
PERSONNEL SAFETY
EQUIPMENT PROTECTION

## Slide 19: Safety for Human life/ Building/Equipments
To save human life from danger of electrical shock or death by blowing a fuse i.e. To provide an alternative path for the fault current to flow so that it will not endanger the user
To protect buildings, machinery & appliances under fault conditions.
To ensure that all exposed conductive parts do not reach a dangerous potential.
To provide safe path to dissipate lightning and short circuit currents.
To provide stable platform for operation of sensitive electronic equipments i.e. To maintain the voltage at any part of an electrical system at a known value so as to prevent over current or excessive voltage on the appliances or equipment

## Slide 20: Over voltage protection
Lightning, line surges or unintentional contact with higher voltage lines can cause dangerously high voltages to the electrical distribution system.
Earthing provides an alternative path around the electrical system to minimize damages in the System

## Slide 21: Earthing

## Slide 22: Earthing

## Slide 23: Types of Earthing
Different types available
Choice depends on local conditions and required function
Simplest form is a single stake
Mostly used for:
  Lightning protection
  Stand alone structures
  Back-up for utility ground

## Slide 24: Types of Earthing
Ground rod group
Typically for lightning protection on larger structures or protection around potential hotspots such as substations.

## Slide 25: Types of Earthing
For areas where there is rock (or other poor conducting material) fairly close to the surface ground plates are preferred as they are more effective
Ground plate

## Slide 26: Types of Earthing
A ground mesh consists of network of bars connected together, this system is often used at larger sites such as electrical substations.
Ground mesh

## Slide 27: Residential Wiring

## Slide 28: Single line diagram of electrical Installation

## Slide 29: Line Diagram of Service line to Main Switch connection

## Slide 30: TYPES Of WIRING
Cleat
Batten
  PVC Wiring
  TRS/CTS Wiring
  Lead Sheath Wiring
Casing Caping
Conduit
  Surface Conduit
    Metal conduit
    P.V.C. conduit
  Concealed Conduit
    Metal conduit
    P.V.C. conduit

## Slide 31: Cleat Wiring

## Slide 32: Batten Wiring

## Slide 33: Batten Wiring

## Slide 34: Wooden Casing and Capping Wiring

## Slide 35: Surface conduit wiring

## Slide 36: Concealed conduit wiring
PVC, or metallic conduit are used Conduit inside the wall
Appearance is good
Protect against fire dust moisture mechanical damage
Less maintenance
Less chance of Fault
Cost is high

## Slide 37: Types of wire used in Residential wiring
Vulcanized Rubber wire
Weather proof wire
Lead covered wire
Mineral insulated copper covered
Poly Vinyl Chloride wire

## Slide 38: Vulcanized Rubber wire